Mediclinic Rooftop PV Projects: Performance Report

Prepared for:

Moshesh Partners

Reference No:

HAR_215_Moshesh Mediclinic Performance Report

26 September 2022

Document Control

| Responsible for | Name | Date | Signature |
| --- | --- | --- | --- |
| Content | Mutali Nepfumbada | 21 September 2022 |  |
| Checked | Thulani Ndaba | 22 September 2022 |  |
| Approved | Adam Terry | 23 September 2022 |  |
| Copyright: | Commercial in Confidence | Document Reference: | HAR_215_Moshesh Mediclinic Monthly Report |
| Signatures in this approval box have checked this document in line with quality procedures requirements This document has been prepared by Harmattan with all reasonable skill and care. The document contains information from sources and data which we believe to be reliable, but we have not confirmed that reliability and make no representation as to their accuracy or completeness. The document is confidential to the Client and Harmattan accepts no responsibility to any third party to whom information in this proposal may be disclosed. No part of this document may be reproduced without the prior written approval of Harmattan. |  |  |  |

Table of Contents

1.	Portfolio Overview	5

1.1.	Scope of Work	5

1.2.	Site Visits	5

1.3.	Report Layout and Risk Assessment Scale	5

2.	Executive Summary	1

2.1.	Performance Summary	1

2.2.	Key Risks, Recommendations & Actions	1

3.	Revenue 	3

3.1.	Revenues	3

4.	Highveld Technical Performance	5

4.1.	Highveld Production Vs Forecast	5

4.2.	Highveld Irradiation Vs Forecast	5

4.3.	Highveld Availability Vs Forecast	6

4.4.	Highveld Performance Ratio Vs Forecast	6

5.	Durbanville Technical Performance	8

5.1.	Durbanville Production Vs Forecast	8

5.2.	Durbanville Irradiation Vs Forecast	9

5.3.	Durbanville Availability Vs Forecast	10

5.4.	Durbanville Performance Ratio Vs Forecast	10

6.	Midstream Technical Performance	12

6.1.	Midstream Production Vs Forecast	12

6.2.	Midstream Irradiation Vs Forecast	12

6.3.	Midstream Availability Vs Forecast	13

6.4.	Midstream Performance Ratio Vs Forecast	13

7.	Hermanus Technical Performance	15

7.1.	Hermanus Production Vs Forecast	15

7.2.	Hermanus Irradiation Vs Forecast	16

7.3.	Hermanus Availability Vs Forecast	16

7.4.	Hermanus Performance Ratio Vs Forecast	17

8.	Vergelegen Technical Performance	18

8.1.	Vergelegen Production Vs Forecast	18

8.2.	Vergelegen Irradiation Vs Forecast	19

8.3.	Vergelegen Availability Vs Forecast	19

8.4.	Vergelegen Performance Ratio Vs Forecast	20

9.	Events	21

9.1.	Health and Safety	21

9.2.	Scheduled Maintenance	21

9.3.	Unscheduled Maintenance	21

9.4.	Spare Parts	22

10.	Project Budget	23

11.	Documents Reviewed	24

List of Figures

Figure 3-1: Revenue Year to Date	3

Figure 4-1: Hermanus Production Vs Forecast	5

Figure 4-2: Highveld Irradiation Vs Forecast	6

Figure 4-3: Highveld Availability Vs Forecast	6

Figure 4-4: Highveld PR Vs Forecast	6

Figure 5-1: Durbanville Production Vs Forecast	8

Figure 5-2: Durbanville Production Vs Forecast	9

Figure 5-3: Durbanville Thermal Test	9

Figure 5-4: Durbanville Irradiation Vs Forecast	10

Figure 5-5: Durbanville Availability Vs Forecast	10

Figure 5-6: Durbanville PR Vs Forecast	10

Figure 6-1: Midstream Production Vs Forecast	12

Figure 6-2: Midstream Irradiation Vs Forecast	13

Figure 6-3: Midstream Availability Vs Forecast	13

Figure 6-4: Midstream PR Vs Forecast	13

Figure 7-1: Hermanus Production Vs Forecast	15

Figure 7-2: Hermanus Inverter Thermal Test	16

Figure 7-3: Hermanus Irradiation Vs Forecast	16

Figure 7-4: Hermanus Availability Vs Forecast	16

Figure 7-5: Hermanus PR Vs Forecast	17

Figure 8-1: Vergelegen Production Vs Forecast	18

Figure 8-2: Vergelegen Production Vs Forecast	19

Figure 8-3: Vergelegen Irradiation Vs Forecast	19

Figure 8-4: Vergelegen Availability Vs Forecast	19

Figure 8-5: Vergelegen PR Vs Forecast	20

List of Tables

Table 1-1: Project Overview	5

Table 1-2: Risk Definitions Key	6

Table 2-1: Key Risk	2

Table 3-1: PPA Rates	3

Table 3-2: Project Revenue Overview	3

Table 4-1: Highveld Project Overview	5

Table 4-2: Hermanus Production and Forecast	5

Table 4-3: Highveld irradiation and Forecast	6

Table 4-4: Highveld Availability and Forecast	6

Table 4-5: Highveld PR and Forecast	6

Table 5-1: Durbanville Project Overview	8

Table 5-2: Durbanville Production and Forecast	8

Table 5-3: Durbanville irradiation and Forecast	10

Table 5-4: Durbanville Availability and Guaranteed	10

Table 5-5: Durbanville PR and Forecast	10

Table 6-1: Midstream Project Overview	12

Table 6-2: Midstream Production and Forecast	12

Table 6-3: Midstream Irradiation and Forecast	13

Table 6-4: Midstream Availability and Guaranteed	13

Table 6-5: Midstream PR and Forecast	13

Table 7-1: Hermanus Project Overview	15

Table 7-2: Hermanus Production and Forecast	15

Table 7-3: Hermanus irradiation and Forecast	16

Table 7-4: Hermanus Availability and Forecast	16

Table 7-5: Hermanus PR and Forecast	17

Table 8-1: Vergelegen Project Overview	18

Table 8-2: Vergelegen Production and Forecast	18

Table 8-3: Vergelegen irradiation and Forecast	19

Table 8-4: Vergelegen Availability and Guaranteed	19

Table 8-5: Vergelegen PR and Forecast	20

Table 9-1: Unscheduled Maintenance Events	22

Table 9-2: Major Spare parts.	22

Table 10-1: Operating Budget	23

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-	-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

-

Abbreviations

| COD | Commercial Operating Date |
| --- | --- |
| HSE | Health and Safety and Environment |
| kWh | Kilo Watt Hour |
| OPEX | Operating expenses |
| PPA | Power Purchase Agreement |
| PR | Performance ratio |
| SCADA | Supervisory control and data acquisition |
| YTD | Year-to-date |

Glossary of Terms

| Actual Production | Production produced in kWh |
| --- | --- |
| Predicted Production | The forecasted P50 production in kWh |
| PR | Actual production divided by weather adjusted production in % |
| Weather Adjusted Predicted | Predicted production adjusted for actual weather in kWh |

# Portfolio Overview

Harmattan Renewables (Harmattan) has been appointed by Moshesh Partners (the Client) to provide asset management support for its rooftop assets at the various Mediclinic sites.

This document is intended to assist the Client in understanding the operational status of its active installations at Vergelegen, Midstream, Hermanus, Highveld, and Durbanville Mediclinic sites including energy production. Table 1-1 provides an overview of the portfolio.

| Name | COD (Commercial Operation Date) | Design Capacity DC/AC (kW) | Achieved Capacity DC/AC (kW) |
| --- | --- | --- | --- |
| Moshesh Mediclinic Durbanville Solar PV | 11 Nov 2021 | 704.6 / 650 | 705.7 / 650 |
| Moshesh Mediclinic Hermanus Solar PV | 10 Mar 2022 | 211.7 / 200 | 211.7 / 220 |
| Moshesh Mediclinic Highveld Solar PV | 30 Mar 2022 | 263 / 250 | 258.9 / 250 |
| Moshesh Mediclinic Midstream Solar PV | 27 Oct 2021 | 227.9 / 200 | 227.9 / 220 |
| Moshesh Mediclinic Vergelegen Solar PV | 28 Oct 2021 | 697.1 / 650 | 689.6 / 650 |

Table 1-1: Project Overview

The projects were all installed by ACES Africa (ACES) who are now acting as the O&M contractor.

## Scope of Work

The scope of work is fully described in Harmattan proposal “HAR_P215_MOSHESH_MediclinicAssetManagement _v2”, dated 15 July 2021”.

## Site Visits

Harmattan has conducted operational monitoring site visits to Vergelegen, and Durbanville and the reports will be provided to the Client. The next site visit will be conducted at Midstream on DATE.

## Report Layout and Risk Assessment Scale

Key findings and recommendations to the Client are highlighted in a summary table at section 2 of the report  The table is colour coded and includes a narrative summary of the overall findings. A fully referenced and detailed summary of the documents reviewed is included in section 9 of the report. Where possible, Harmattan will confirm whether review items are consistent with market norms / standards and across all Project documentation. Where Harmattan identifies an omission, error, inconsistency, or deviation from our expectations, an issue will be flagged, analysed, and assigned a risk rating as outlined in Table 1-2.

For all items, where an issue is identified, a risk category and colour code are allocated. Categorisation is achieved by making a qualitative assessment of the probability of the occurrence of the issue and the severity of the impact of the issue and allocating a tag Critical (C) / High (H) / Medium (M) / Low (L) / Negligible (N) and associated colour code to each issue (together with a brief explanation of why the tags were chosen).  These tags are then multiplied in a range of combinations to yield a qualitative risk categorisation (see graphic below). This categorisation of risk allows for the prioritisation of the issues originally identified and brings a degree of focus to the subsequent mitigation process. If no risk is present / relevant, then the categorisation is summarised as 'Not Applicable' (N/A). Harmattan highlights that a simple, non-numerical, approach has been adopted to maintain the simplicity and functionality of the method and to avoid unproductive debates around the calibration of the categorisation components.

| Key |  |  | Definition | Description |  |
| --- | --- | --- | --- | --- | --- |
| C |  |  | Critical | Risk of critical negative influence on project/investment outcome |  |
| H |  |  | High | Risk of high negative influence on project/investment outcome |  |
| M |  |  | Medium | Risk of medium negative influence on project/investment outcome. |  |
| L |  |  | Low | Risk of low negative influence on project/investment outcome. |  |
| N |  |  | Negligible | Risk of negligible negative influence on project/investment outcome. |  |
| N/A | Not Applicable | No risk present/relevant. |  |  |
| TBC |  |  | Awaiting Information | Additional information required to enable Harmattan to opine on the risk. |  |

Table 1-2: Risk Definitions Key

# Executive Summary

## Performance Summary

The following section describes August 2022 performance of the sites.

      - Moshesh Mediclinic Vergelegen Solar PV

- Production is {{VERP}} KWh with a variance of {{VERPV}} % below the P50 forecast.

- Irradiation is {{VERI}} kWh/m2 with a variance of {{VERIV}} % below P50 forecast.

- Availability is {{VERA}} % with a variance of {{VERAV}} % above the warranted availability.

- PR is {{VERPR}} % with a variance of {{VERPRV}} % below warranted availability.

- Revenue is R{{VERZARLT}} with a variance of {{VERZARVLT}} % below forecast.

    - Moshesh Mediclinic Durbanville Solar PV

- Production is {{DURP}} KWh with a variance of {{DURPV}} % below the P50 forecast.

- Irradiation is {{DURI}} kWh/m2 with a variance of {{DURIV}} % below P50 forecast.

- Availability is {{DURA}} % with a variance of {{DURAV}} % above the warranted availability.

- PR is {{DURPR}} % with a variance of {{DURPR}} % below warranted availability.

- Revenue is R{{DURZARLT}} with a variance of {{DURZARVLT}} % below forecast.

    - Moshesh Mediclinic Midstream Solar PV

- Production is {{MIDP}} KWh with a variance of {{MIDPV}} % below the P50 forecast.

- Irradiation is {{MIDI}} kWh/m2 with a variance of {{MIDIV}} % below P50 forecast.

- Availability is {{MIDA}} % with a variance of {{MIDAV}} % above the warranted availability.

- PR is {{MIDPR}} % with a variance of {{MIDPRV}} % below warranted availability.

- Revenue is R{{MIDZARLT}} with a variance of {{MIDZARVLT}} % below forecast.

    - Moshesh Mediclinic Hermanus Solar PV

- Production is {{HERP}} KWh with a variance of {{HERPV}} % below the P50 forecast.

- Irradiation is {{HERI}} kWh/m2 with a variance of {{HERIV}} % below P50 forecast.

- Availability is {{HERA}} % with a variance of {{HERAV}} % above the warranted availability.

- PR is {{HERPR}} % with a variance of {{HERPRV}} % below warranted availability.

- Revenue is R{{HERZARLT}} with a variance of {{HERZARVLT}} % below forecast.

    - Moshesh Mediclinic Highveld Solar PV

- Production is {{HIGP}} KWh with a variance of {{HIGPV}} % below the P50 forecast.

- Irradiation is {{HIGI}} kWh/m2 with a variance of {{HIGIV}} % below P50 forecast.

- Availability is {{HIGA}} % with a variance of {{HIGAV}} % above the warranted availability.

- PR is {{HIGPR}} % with a variance of {{HIGPRV}} % below warranted availability.

- Revenue is R{{HIGZARLT}} with a variance of {{HIGZARVLT}} % below forecast.

## Key Risks, Recommendations & Actions

The following key risk were identiﬁed in report month.

| Key Risks | Descriptions | Risk Rating | Actions | Recommendation |
| --- | --- | --- | --- | --- |
| Plant Underperformance | All sites have inadequate performance compared to the predicted energy. The Operator has stated that the inadequate performance is due to curtailment during load shedding and poor irradiance due to weather conditions at each site. | H | Harmattan has requested the Operator to provide all the unscheduled and maintenance report and also give details on why the plant is curtailed during loadshedding | Harmattan recommends using the emergency generator as a reference to continue operation during a load shedding event. The ace will need to determine if this is possible. Harmattan also recommends running the yield simulation to confirm if the forecasts are correct. |
| Shading | Harmattan have noted that some module in Durbanville site is shaded by nearby trees resulting in module damage and a loss in production. | H | According to the report submitted, no action has been taken to solve this problem. | Harmattan would recommend cutting down the trees nearby. |
| Inverters overheating | The inverter at Vergelegen overheats due to poor ventilation, causing production losses. Harmattan notes that the inverters were not operated above 60 ˚C at the beginning of the fall and winter seasons. We note that with the transition to the summer season, the inverter temperature increases and is operated above the maximum temperature. | H | The Operators have stated that Mediclinic will install the ventilation system, but this has not happened. | Harmattan recommends that Aces conduct further heat testing at other sites to determine if they are experiencing similar problems. Harmattan recommends that Aces Mediclinic submit specifications for the cooling required to keep the inverter at a safe operating temperature. Harmattan will review the specification and costing. |
| Performance Guarantee | Harmattan note that Durbanville, Vergelegen, and Midstream started operation in October 2021, we do not have irradiance data until March 2022. We cannot use the following formula to adjust generation for 12 months. Generationadjusted =GenerationexpectedkWh*IrradianceSatelliteWhm2IrradiancePredictedWhm2 Performance Guarantee after Services Start Date The Operator guarantees to the Owner that the Facility will reach a minimum of 90% of “Generation Adjusted” in a consecutive period of 12 months. | H | No action has been taken | Harmattan recommends: Only consider data from April 2022 to November 2022 for generation adjustment. Inquire if ACES can use satellite data from another site near the Moshesh projects. |

Table 2-1: Key Risk

-

# Revenue

The revenue is based on the actual production and the agreed PPA rate between Mediclinic and Moshes. The forecasted revenue is based on the P50 Helioscope simulation done in the preconstruction phase of the project.

All projects directly supply electricity to their respective Mediclinics via a PPA. A summary of the PPA rates is shown in [insert table], confirm PPA rate and year it’s valid for.

| Plants | PPA Rates (ZAR/ kWh) | Year |
| --- | --- | --- |
| Durbanville | 0.6066 | 11 November 2021 – 11 November 2022 |
| Vergelegen | 0.6148 | 28 October 2021 – 28 October 2022 |
| Highveld | 0.6589 | 30 March 2022- 30 March 2023 |
| Midstream | 0.6741 | 27 October 2021 – 27 October 2022 |
| Hermanus | 0.7944 | 10 March 2022- 10 March2023 |

Table 3-1: PPA Rates

Forecast revenues are based upon [pre-construction yield estimates] and have not been adjusted to reflect received irradiation.

Actual revenue is based upon…. [SCADA data for production and the PPA rates] shown above.

Weather adjusted forecast is the predicted production adjusted for actual weather in kWh

## Revenues

The following graph shows the revenue against the budgeted revenue since COD.

{{Revenue}}

Figure 3-1-: Revenue Year to Date

| Revenue (ZAR) |  |  |  |
| --- | --- | --- | --- |
| Plants | Actual | Forecast | Delta (%) |
| Durbanville | {{DURZARTOT}} | {{DURZARFOR}} | {{DURZARV}} |
| Vergelegen | {{VERZARTOT}} | {{VERZARFOR}} | {{VERZARV}} |
| Highveld | {{HIGZARTOT}} | {{HIGZARFOR}} | {{HIGZARV}} |
| Midstream | {{MIDZARTOT}} | {{MIDZARFOR}} | {{MIDZARV}} |
| Hermanus | {{HERZARTOT}} | {{HERZARFOR}} | {{HERZARV}} |

Table 3-2: Project Revenue Overview

Given the above, the average underperformance is XX. The following chapters investigate the cause of the underperformance in order of worst to best performing project.

#### Possible Causes

Harmattan has investigated possible sources of underperformance, these focus on resource, load shedding and plant performance.

Harmattan has noted that all of the plants were not meeting the P50 projection stated in the Helioscope Simulation. We contacted the operator to get more information on the possible causes of the underperformance, the operator has stated that load shedding is a major factor for the underperformance and also low irradiation. No major faults were recorded that have resulted in the underperformance. Harmattan has investigated the losses using SCADA data and analysing the technology installed.

Another reason for the lower than forecast production is load shedding.  Load shedding causes the power plant's inverter to shut down, resulting in production losses.

Grid-connected PV plants are usually programmed to shut down during load shedding. This is due to international safety standards. Solar modules generate DC electricity, but this must be converted to AC to be used in buildings. For this purpose, solar inverters are used to convert the electricity.

In the event of a grid outage (e.g., Eskom load shedding), the solar inverters are designed to shut down. This is to protect the grid personnel working on the transmission lines during the outage. If the buildings continue to generate power during a grid outage and potentially feed power to the national grid, this could be fatal to maintenance personnel who are unaware that power is flowing in the lines when the grid is down.

# Highveld Technical Performance

The following tables and figures on the technical performance and forecast data provide information on the production, irradiation, availability, and performance ratio of the plant compared to the forecast.

| Project Overview |  |
| --- | --- |
| Capacity (kW DC): | 262.7 |
| Technology | Solar |
| Project Company: | Moshesh Solar PV 1 (Pty) Ltd |
| Address: | 46 Barney Molokwane, Trichardt South Africa |
| Commercial Operation Date | 30 Mar 2022 |

Table 4-1: Highveld Project Overview

## Highveld Production Vs Forecast

The following tables describe the production of the plant since April 2022 COD. Production is compared to the P50 Helioscope forecast and the weather-adjusted forecast.

Month; Production (kWh); Actual vs Weather Adjusted Forecast (%). Original Forecast; Weather Adjusted Forecast; Actual Production. {%tr for item in HIGPtable_contents%}. {{item.Date}}; {{item.HIGPF}}; {{item.HIGPW}}; {{ item.HIGPA}}; {{item.HIGPV}}; {{item.HIGPWV}}. {%tr endfor%}. Total; {{HIGPFTOT}}; {{HIGPWTOT}}; {{HIGPATOT}}; {{HIGPVTOT}}; {{HIGPWVTOT}}.

Table 4-2: Hermanus Production and Forecast

{{ HIGPImage}} Figure 4-1: Hermanus Production Vs Forecast

Total production since COD is 119827.04 kWh with a 26.1% deviation from the P50 forecast and 13.12% from the weather-adjusted forecast.

The weather-adjusted forecast is lower than the P50 forecast, which means that the generation could not meet the P50 forecast due to the bad weather conditions. The high deviation from the weather-adjusted forecast also means that curtailment of the power plant during load shedding played a role in the shortfall, as did unplanned maintenance.

Harmattan recommends that the Operator provide unplanned maintenance events to verify losses caused by disturbances.

## Highveld Irradiation Vs Forecast

The following table and graph describe the irradiance of the site compared to the Helioscope P50 prediction. Harmattan notes that the irradiance measurement is satellite-based.

The site has been measuring irradiance since April to the present, and no irradiance data is available prior to that time.

| Irradiation (kWh/m2). Month; Actual; Forecast; Delta (%). {%tr for item in HIGItable_contents%}. {{item.Date}}; {{ item. HIGIA}}; {{ item. HIGIF }}; {{item. HIGIV}}. {%tr endfor %}. | {{HIGIImage}} |
| --- | --- |
| Table 4-3: Highveld irradiation and Forecast | Figure 4-2: Highveld Irradiation Vs Forecast |

The above table and figure show that the solar irradiance is below the forecast from April 2021 to July 2022 and improves above the forecast in August with a deviation of 5.05%. The irradiance of the site is poor and deviates greatly from the forecast.

Harmattan therefore recommends that an operating yield of the site be determined to confirm the irradiance.

## Highveld Availability Vs Forecast

The following table and chart describe the availability of the plant since COD, comparing the availability of the plant with the guaranteed minimum availability of 95%.

| Availability (%). Month; Actual; Forecast; Delta (%). {%tr for item in HIGAtable_contents%}. {{item.Date}}; {{ item. HIGAA}}; {{ item. HIGAF }}; {{item. HIGAV}}. {%tr endfor %}. | {{HIGAImage}} |
| --- | --- |
| Table 4-4: Highveld Availability and Forecast | Figure 4-3: Highveld Availability Vs Forecast |

From the table and chart above, it appears that the power plant has not met the minimum 95% availability from June to the present. Harmattan cannot confirm if the unavailability of the power plant is due to unscheduled maintenance as no report has been submitted.

The Operator has indicated that the availability of the power plant was mainly affected by load shedding. Harmattan recommends that the Operator submit the unscheduled maintenance reports for the site to confirm this.

## Highveld Performance Ratio Vs Forecast

The following table and chart describe the availability of the plant since COD, comparing the availability of the plant with the guaranteed minimum availability of 95%.

| Performance Ratio (%). Month; Actual; Forecast; Delta (%). {%tr for item in HIGPRtable_contents%}. {{item.Date}}; {{ item. HIGPRA}}; {{item. HIGPRF }}; {{item. HIGPRV}}. {%tr endfor %}. | {{HIGPRImage}} |
| --- | --- |
| Table 4-5: Highveld PR and Forecast | Figure 4-4: Highveld PR Vs Forecast |

Harmattan notes that the plant's performance was below the expected forecast, with a maximum deviation of -21.43% in July and a minimum deviation of -11.56% in April.

Harmattan notes that the power plant's performance has not improved since COD until today. The Operator has stated that the inadequate performance of the power plant is due to the bad weather conditions, which have resulted in lower irradiation than expected, as well as load shedding, which leads to production losses because the inverter cannot be put into operation for safety reasons.

# Durbanville Technical Performance

The following tables and figures on the technical performance and forecast data provide information on the production, irradiation, availability, and performance ratio of the plant compared to the forecast.

| Project Overview |  |
| --- | --- |
| Capacity (kW DC): | 705.7 |
| Technology | Solar |
| Project Company: | Moshesh Solar PV 1 (Pty) Ltd |
| Address: | Wellington Road Durbanville South Africa |
| Commercial Operation Date | 11 Nov 2021 |

Table 5-1: Durbanville Project Overview

## Durbanville Production Vs Forecast

The following tables describe the production of the plant since COD. Production is compared to the P50 Helioscope forecast and the weather-adjusted forecast.

Month; Production (kWh); Actual vs Original Forecast (%); Actual vs Weather Adjusted Forecast (%). Original Forecast; Weather Adjusted Forecast; Actual Production. {%tr for item in DURPtable_contents%}. {{item.Date}}; {{item.DURPF}}; {{item.DURPW}}; {{item.DURPA}}; {{item.DURPV}}; {{item.DURPWV}}. {%tr endfor%}. Total; {{DURPFTOT}}; {{DURPWTOT}}; {{DURPATOT}}; {{DURPVTOT}}; {{DURPWVTOT}}.

Table 5-2: Durbanville Production and Forecast

{{ DURPImage}} Figure 5-1: Durbanville Production Vs Forecast

Total production since COD is 725443.1 kWh with a variance of 21.29% below the P50 forecast and 21.56% below the weather-adjusted forecast. This shows that weather conditions had only a minor impact on the failure to meet the P50 forecast. The weather-adjusted forecast shows slightly higher production than the P50 forecast.

The loss of production cannot be attributed solely to low irradiance and curtailment, as the variance is high. We note that tree shade and inverter faults may have influenced the high underproduction of the system.

The following image shows the tree shade in Durbanville, which was detected in March 2022 during

the on-site inspection.

Figure 5-2-: Durbanville Production Vs Forecast

Harmattan also reviewed the inverter's thermal test to determine if the production failure was caused by the inverter's inefficiency at an operating temperature above 60 ˚C. According to the thermal test conducted on 20 April 2022, the maximum operating temperature is 36.0 ˚C, as shown below. No other inverter was observed to exceed the operating temperature of 36.0˚C.

Figure 5-3: Durbanville Thermal Test

Harmattan notes that the inverters are operating within the expected temperature range, as no inverter was found to exceed the maximum temperature range of 60 ˚C. Harmattan recommends that the temperature also be measured during the summer season, as the inverter's operating temperature may rise during hot weather.

## Durbanville Irradiation Vs Forecast

The following table and graph describe the irradiance of the site compared to the Helioscope P50 prediction. Harmattan notes that the irradiance measurement is satellite-based. The site has been measuring irradiance since April to the present, and no irradiance data is available prior to that time.

| Irradiation kWh/m2. Month; Actual; Forecast; Delta (%). {%tr for item in DURItable_contents%}. {{item.Date}}; {{ item. DURIA}}; {{ item. DURIF }}; {{item. DURIV}}. {%tr endfor %}. | {{DURIImage}} |
| --- | --- |
| Table 5-3: Durbanville irradiation and Forecast | Figure 5-4: Durbanville Irradiation Vs Forecast |

The above table and figure show that the solar irradiance from April 2021 to August 2022 is below the forecast except for the month of June 2022. In the absence of data from previous months, Harmattan cannot confirm whether the site has experienced good or poor solar radiation since COD.

## Durbanville Availability Vs Forecast

The following tables and figures on the technical performance and forecast data provide information on the production, irradiation, availability, and performance ratio of the plant compared to the forecast.

| Availability (%). Month; Actual; Forecast; Delta (%). {%tr for item in DURAtable_contents%}. {{item.Date}}; {{ item. DURAA}}; {{ item. DURAF }}; {{item. DURAV}}. {%tr endfor %}. | {{DURAImage}} |
| --- | --- |
| Table 5-4: Durbanville Availability and Guaranteed | Figure 5-5: Durbanville Availability Vs Forecast |

From the above table and diagram, we can see that the plant has reached the minimum availability of 95% for several months since COD. We note that the plant did not reach the minimum availability in January 2022, May 2022 and July 2022 with a deviation of 4% to 7% from the guaranteed availability.

We also note that the plant did not meet the guaranteed availability in November 2021, but this is due to the fact that the plant was only in operation for 19 days, resulting in a misstatement of 68.81% availability.

Harmattan cannot confirm whether the power plant's unavailability was due to unscheduled maintenance, as only 3 unscheduled events were reported. The Operator has indicated that the availability of the power plant was mainly affected by load shedding. Harmattan recommends that the Operator submit the unscheduled maintenance reports for the site to confirm that the unavailability was due solely to load shedding.

## Durbanville Performance Ratio Vs Forecast

The following table and chart compare the Scada Performance Ratio with the monthly forecast P50 PR of the Helioscope Forecast report.

| Performance Ratio (%). Month; Actual; Forecast; Delta (%). {%tr for item in DURPRtable_contents%}. {{item.Date}}; {{ item. DURPRA}}; {{item. DURPRF }}; {{item. DURPRV}}. {%tr endfor %}. | {{DURPRImage}} |
| --- | --- |
| Table 5-5: Durbanville PR and Forecast | Figure 5-6: Durbanville PR Vs Forecast |

From the chart and table above, the performance ratio from April to present has fallen short of projections, ranging from -9.59% to -28.05% variance.

Harmattan notes that the power plant's Performance Ratio has not improved, and due to a lack of data, cannot confirm whether it has lagged behind projections since COD.

The Operator has stated that the underperformance of the power plant is due to poor weather conditions that have resulted in lower irradiation than expected, as well as load shedding that results in production outages because the inverter cannot be put into operation for safety reason.

# Midstream Technical Performance

The following tables and figures on the technical performance and forecast data provide information on the production, irradiation, availability, and performance ratio of the plant compared to the forecast.

| Project Overview |  |
| --- | --- |
| Capacity (kW DC): | 227.9 |
| Technology | Solar |
| Project Company: | Moshesh Solar PV 1 (Pty) Ltd |
| Address: | Midstream Drive, Hill Boulevard Midstream Estate, Olifantsfontein. - South Africa |
| Commercial Operation Date | 27 Oct 2021 |

Table 6-1: Midstream Project Overview

## Midstream Production Vs Forecast

The following tables describe the production of the plant since COD. Production is compared to the P50 Helioscope forecast and the weather-adjusted forecast.

Month; Production (kWh); Actual vs Original Forecast (%); Actual vs Weather Adjusted Forecast (%). Original Forecast; Weather Adjusted Forecast; Actual Production. {%tr for item in MIDPtable_contents%}. {{item.Date}}; {{item.MIDPF}}; {{item.MIDPW}}; {{item.MIDPA}}; {{item.MIDPV}}; {{item.MIDPWV}}. {%tr endfor%}. Total; {{MIDPFTOT}}; {{MIDPWTOT}}; {{MIDPATOT}}; {{MIDPVTOT}}; {{MIDPWVTOT}}.

Table 6-2: Midstream Production and Forecast

{{ MIDPImage}} Figure 6-1: Midstream Production Vs Forecast

Total production since COD is 286610.1kWh with a variance of 8.18% below forecast production and 9.16% below weather adjusted forecast.

The weather-adjusted generation is greater than the P50 forecast, which means that the power plant could have met and exceeded the P50 generation if the power plant had not been curtailed during load shedding, which would have resulted in production losses.

## Midstream Irradiation Vs Forecast

The following table and graph describe the irradiance of the site compared to the Helioscope P50 prediction. Harmattan notes that the irradiance measurement is satellite-based.

The site has been measuring irradiance since April to the present, and no irradiance data is available prior to that time.

| Irradiation (kWh/m2). Month; Actual; Forecast; Delta (%). {%tr for item in MIDItable_contents%}. {{item.Date}}; {{ item. MIDIA}}; {{ item. MIDIF }}; {{item. MIDIV}}. {%tr endfor %}. | {{MIDIImage}} |
| --- | --- |
| Table 6-3: Midstream Irradiation and Forecast | Figure 6-2: Midstream Irradiation Vs Forecast |

The above table and figure show that solar irradiance from April 2022 to August 2022 is below projections. In the absence of data from previous months, Harmattan cannot confirm whether the facility has experienced good or poor solar irradiance levels since COD. We can only state that the irradiance is poor compared to the P50 irradiance.

## Midstream Availability Vs Forecast

The following table and chart describe the availability of the plant since COD, comparing the availability of the plant with the guaranteed minimum availability of 95%.

| Availability (%). Month; Actual; Forecast; Delta (%). {%tr for item in MIDAtable_contents%}. {{item.Date}}; {{ item. MIDAA}}; {{ item. MIDAF }}; {{item. MIDAV}}. {%tr endfor %}. | {{MIDAImage}} |
| --- | --- |
| Table 6-4: Midstream Availability and Guaranteed | Figure 6-3: Midstream Availability Vs Forecast |

From the above table and graph, we can see that the plant has reached the minimum availability of 95% for several months since COD.

We note that the plant did not reach the minimum availability in January 2022, February 2022 and July 2022 with a deviation of -1 to -32% from the guaranteed availability. We also note that the plant has a high deviation in February 2022. Harmattan cannot confirm whether the high deviation is due to a fault in the SCADA system or caused by unplanned maintenance in February, as no maintenance report and checklist were provided.

The Operator has only stated that the availability of the power plant was mainly affected by load shedding. Harmattan recommends that the Operator submit the unscheduled maintenance reports for the site to confirm that the unavailability was due solely to load shedding.

## Midstream Performance Ratio Vs Forecast

The following table and chart compare the Scada Performance Ratio with the monthly forecast P50 PR of the Helioscope Forecast report.

| Performance Ratio (%). Month; Actual; Forecast; Delta (%). {%tr for item in MIDPRtable_contents%}. {{item.Date}}; {{ item. MIDPRA}}; {{item. MIDPRF }}; {{item. MIDPRV}}. {%tr endfor %}. | {{MIDPRImage}} |
| --- | --- |
| Table 6-5: Midstream PR and Forecast | Figure 6-4: Midstream PR Vs Forecast |

From the chart and table above, the performance ratio from May to date has fallen short of projections, ranging from -4.13% to -10.86%. Harmattan notes that the power plant's Performance Ratio has not improved, and due to a lack of data, cannot confirm whether it has lagged behind projections since COD.

The Operator has stated that the inadequate performance of the power plant is due to poor weather conditions that have resulted in lower irradiation than expected, as well as load shedding that results in production outages because the inverter cannot be put into operation for safety reasons.

# Hermanus Technical Performance

Technical performance tables and forecast figures below give details on plant Gross Generation, Irradiation, Availability and Performance Ratio compared against the Forecast/warranted values, then analyse the results and give recommendations.

| Project Overview |  |
| --- | --- |
| Capacity (kW DC): | 219.4 |
| Technology | Solar |
| Project Company: | Moshesh Solar PV 1 (Pty) Ltd |
| Address: | Ravenscroft Rd Hermanus – 7200 – South Africa |
| Commercial Operation Date | 10 Mar 2022 |

Table 7-1: Hermanus Project Overview

## Hermanus Production Vs Forecast

The following tables describe the production of the plant since March 2022 COD. Production is compared to the P50 Helioscope forecast and the weather-adjusted forecast.

Month; Production (kWh); Actual vs Original Forecast (%); Actual vs Weather Adjusted Forecast (%). Original Forecast; Weather Adjusted Forecast; Actual Production. {%tr for item in HERPtable_contents%}. {{item.Date}}; {{item.HERPF}}; {{item.HERPW}}; {{ item.HERPA}}; {{item.HERPV}}; {{item.HERPWV}}. {%tr endfor%}. Total; {{HERPFTOT}}; {{HERPWTOT}}; {{HERPATOT}}; {{HERPVTOT}}; {{HERPWVTOT}}.

Table 7-2: Hermanus Production and Forecast

{{ HERPImage}} Figure 7-1: Hermanus Production Vs Forecast

Total production since COD is 112141.72kWh with a deviation of 6.48% below the P50 forecast and 3.83% below the weather-adjusted forecast.

This shows that weather conditions had an impact on the power plant not meeting the P50 forecast, but we note that weather cannot be the only reason for the low production, as the weather-adjusted deviation is high. The Operator has stated that the high deviation may be due to load shedding that resulted in production outages.

Harmattan also reviewed the inverter's thermal test to determine if the production failure was caused by the inverter's inefficiency at an operating temperature above 60 ˚C. According to the thermal test conducted on 24 August 2022, the maximum operating temperature is 34.9 ˚C, as shown below. No other inverter was observed to exceed the operating temperature of 34.9 ˚C.

Figure 7-2: Hermanus Inverter Thermal Test

Harmattan notes that the inverters are operating within the expected temperature range, as no inverter was found to exceed the maximum temperature range of 60 ˚C. Harmattan recommends that the temperature also be measured during the summer season, as the inverter's operating temperature may rise during hot weather.

## Hermanus Irradiation Vs Forecast

The following table and graph describe the irradiance of the site compared to the Helioscope P50 prediction. Harmattan notes that the irradiance measurement is satellite-based.

The site has been measuring irradiance since April to the present, and no irradiance data is available prior to that time.

| Irradiation (kWh/m2). Month; Actual; Forecast; Delta (%). {%tr for item in HERItable_contents%}. {{item.Date}}; {{ item. HERIA}}; {{ item. HERIF }}; {{item. HERIV}}. {%tr endfor %}. | {{HERIImage}} |
| --- | --- |
| Table 7-3: Hermanus irradiation and Forecast | Figure 7-3: Hermanus Irradiation Vs Forecast |

The table and figure above show that the irradiation is below forecast in April 2021 to July 2022 and above in August 2022, May 2022 and June 2022.

## Hermanus Availability Vs Forecast

The following table and chart describe the availability of the plant since COD, comparing the availability of the plant with the guaranteed minimum availability of 95%.

| Availability (%). Month; Actual; Forecast; Delta (%). {%tr for item in HERAtable_contents%}. {{item.Date}}; {{ item. HERAA}}; {{ item. HERAF }}; {{item. HERAV}}. {%tr endfor %}. | {{HERAImage}} |
| --- | --- |
| Table 7-4: Hermanus Availability and Forecast | Figure 7-4: Hermanus Availability Vs Forecast |

From the above table and chart, it appears that the power plant has not met the minimum availability of 95% since COD for some months. Harmattan cannot confirm if the unavailability of the power plant is due to unscheduled maintenance as no report has been submitted. The Operator has indicated that the availability of the power plant was mainly affected by load shedding. Harmattan recommends that the Operator submit the unscheduled maintenance reports for the site to confirm this.

## Hermanus Performance Ratio Vs Forecast

The following table and chart compare the Scada Performance Ratio with the monthly forecast P50 PR of the Helioscope Forecast report.

| Performance Ratio (%). Month; Actual; Forecast; Delta (%). {%tr for item in HERPRtable_contents%}. {{item.Date}}; {{ item. HERPRA}}; {{item. HERPRF }}; {{item. HERPRV}}. {%tr endfor %}. | {{HERPRImage}} |
| --- | --- |
| Table 7-5: Hermanus PR and Forecast | Figure 7-5: Hermanus PR Vs Forecast |

Harmattan notes that the power plant's performance from April 2022 to July 2022 was below the expected forecast, with a variance of -5.18% to -12.35%.

Harmattan notes that the power plant's performance ratio improved in August 2022. The Operator has stated that the inadequate performance of the power plant was due to poor weather conditions, which resulted in lower irradiation than expected, and load shedding, which resulted in production losses because the inverter could not be operated for safety reasons.

# Vergelegen Technical Performance

The following section summarises the Vergelegen project and highlights its technical performance. Key Performance indicators including  production, irradiation, availability, and performance ratio were assessed from the SCADA , and compared to the forecast.

| Project Overview |  |
| --- | --- |
| Capacity (kW DC): | 689.6 |
| Technology | Solar |
| Project Company: | Moshesh Solar PV 1 (Pty) Ltd |
| Address: | Vergelegen, Main Road Somerset West South Africa |
| Commercial Operation Date | 28 Oct 2021 |

Table 8-1: Vergelegen Project Overview

## Vergelegen Production Vs Forecast

The following table describes the production of the project. Production was measured from COD to August 2022 and compared to the P50 forecast.

Month; Production (kWh); Actual vs Original Forecast (%); Actual vs Weather Adjusted Forecast (%). Original Forecast; Weather Adjusted Forecast; Actual Production. {%tr for item in VERPtable_contents%}. {{item.Date}}; {{item.VERPF}}; {{item.VERPW}}; {{ item.VERPA}}; {{item.VERPV}}; {{item.VERPWV}}. {%tr endfor%}. Total; {{VERPFTOT}}; {{VERPWTOT}}; {{VERPATOT}}; {{VERPVTOT}}; {{VERPWVTOT}}.

Table 8-2: Vergelegen Production and Forecast

{{VERPImage}} Figure 8-1: Vergelegen Production Vs Forecast

Total production since COD is 840,969 kWh with a variance of 5.22 % below the original forecast and 4.99% below the weather adjusted forecast.

We found that the production is below the P50 forecast because of lower irradiance than expected. This is confirmed by the weather-adjusted forecast, which shows lower production than the actual production.

The following figure describes the inverter temperature at Vergelegen. The thermal image was taken on March 30, 2022, and shows that the inverter is operating at 50 ˚C, which is close to the maximum operating temperature of 60 ˚C.

The high operating temperature of the inverter has implications for production. Harmattan notes that the inverter has not exceeded the maximum temperature of 60 ˚C, but points out that this might change during the summer months.

Figure 8-2-: Vergelegen Production Vs Forecast

Harmattan notes that the Operator (Aces) has proposed that Mediclinic provide additional ventilation to the room where the inverters are located. This has not been done because the winter season has allowed for additional cooling of the inverter.

Harmattan recommends that the Operator provide Mediclinic with a specification for the required cooling of the equipment and conduct further thermal testing at the other sites. Harmattan will review the specification and costing provided by ACES.

## Vergelegen Irradiation Vs Forecast

The following table and graph describe the irradiance of the site compared to the Helioscope P50 prediction. Harmattan notes that the irradiance measurement is satellite-based. The site has been measuring irradiance since April to the present, and no irradiance data is available prior to that time.

| Irradiation (kWh/m2). Month; Actual; Forecast; Delta (%). {%tr for item in VERItable_contents%}. {{item.Date}}; {{ item. VERIA}}; {{ item. VERIF}}; {{item. VERIV}}. {%tr endfor %}. | {{VERIImage}} |
| --- | --- |
| Table 8-3: Vergelegen irradiation and Forecast | Figure 8-3: Vergelegen Irradiation Vs Forecast |

From the above table and figure, solar radiation was above forecast in May, June, and August, while it was below forecast in April and July. In the absence of data from previous months, Harmattan cannot confirm whether solar irradiation has been good or bad since COD.

## Vergelegen Availability Vs Forecast

The following table and chart describe the availability of the plant since COD, comparing the availability of the plant with the guaranteed minimum availability of 95%.

| Availability (%). Month; Actual; Forecast; Delta (%). {%tr for item in VERAtable_contents%}. {{item.Date}}; {{ item. VERAA}}; {{ item. VERAF}}; {{item. VERAV}}. {%tr endfor %}. | {{VERAImage}} |
| --- | --- |
| Table 8-4: Vergelegen Availability and Guaranteed | Figure 8-4: Vergelegen Availability Vs Forecast |

From the above table and graph, we can see that the plant has reached the minimum availability of 95% for several months since COD. We note that the plant did not reach the minimum availability in November 2021, June 2022, July 2022 and August 2022 with a deviation of 3 to 4% from the guaranteed availability.

We also note that the plant did not meet guaranteed availability in October 2021, but this is due to the fact that the plant was only in operation for four days, resulting in a misstatement of 15.83% availability. Harmattan cannot confirm whether the power plant's unavailability was due to unscheduled maintenance, as only one unscheduled event was reported.

The Operator has indicated that the availability of the power plant was mainly affected by load shedding. Harmattan recommends that the Operator submit the unscheduled maintenance reports for the site to confirm that the unavailability was due solely to load shedding

## Vergelegen Performance Ratio Vs Forecast

The following table and chart compare the Scada Performance Ratio with the monthly forecast P50 PR of the Helioscope Forecast report.

| Performance Ratio (%). Month; Actual; Forecast; Delta (%). {%tr for item in VERPRtable_contents%}. {{item.Date}}; {{ item. VERPRA}}; {{item. VERPRF }}; {{item. VERPRV}}. {%tr endfor %}. | {{VERPRImage}} |
| --- | --- |
| Table 8-5: Vergelegen PR and Forecast | Figure 8-5: Vergelegen PR Vs Forecast |

From the chart and table above, it appears that the performance ratio from April to present has fallen short of projections, ranging from -2.99% to -16.58%. Harmattan notes that the power plant's Performance Ratio has not improved. Due to a lack of data, we cannot confirm whether it has lagged behind projections since COD.

The Operator has stated that the inadequate performance of the power plant is due to poor weather conditions that have resulted in lower irradiation than expected, as well as load shedding that results in production outages because the inverter cannot be put into operation for safety reasons.

# Events

## Health and Safety

No health and safety incidence were reported based on the information provided by the Operator.

## Scheduled Maintenance

Harmattan notes that the Operator has only submitted the inspection list for Durbanville, Hermanus and Vergelegen. No issues have been identified for Hermanus and Vergelegen. In Durbanville we have noticed that nearby trees are shading the panels . The Operator has not provided any recent reports indicating whether this problem has been corrected.

Module cleaning was not performed in Hermanus and Durbanville since COD because the modules were clean. For Vergelegen, module cleaning was performed on March 31, 2022. The latest status from the operator is that the modules are still clean. No report was submitted for Midstream and Highveld.

## Unscheduled Maintenance

The following table describes the unscheduled maintenance activities that have occurred since COD.

| Date Occurred | Plant | Events | Description | Resolution |
| --- | --- | --- | --- | --- |
| 9/5/2022 | Durbanville | The communication is down in, and the inverters are not producing. | Communication between inverters and logger is interrupted and inverters show no production - idle status. It has been determined that UPS has failed for communication on block 3, causing communication to be interrupted. The UPS has failed without external causes. | The UPS was repaired on 10 May 2022. The estimated production downtime is 2MW. |
| 9/5/2022 | Durbanville | Inverter 5 - no production - string fault. | The inverter went into fault mode because one string had an abnormal voltage reading to earth. String 5.4.1 had an insulation fault and there was a voltage leakage into the earth system. The fault could not be corrected within 24 hours because no team was available at that time to lift the equipment and find the fault. | On 27 May 2022, the faulty string was disconnected from the inverter to resume production, and a new connector was attached to the undamaged piece of cable. The fault resulted in a production loss of 175 kWh. |
| 3/7/2022 | Durbanville | Inverters 4 to 7 no production | No link between the logger and inverters 4 to 7. The UPS for the PA link has failed | On 4 July 2022, a new part (UPS) was installed The production loss hour is 1.1MW |
| 23/08/2022 | Durbanville | Theft | The main earthing cable of the solar system has been stolen (7 meters) behind the green tanks on the roof slab. | The earthing cable parts that was stolen have been replaced. Harmattan have also submitted incident to the insurer to understand the excess on the claim. The insurer has stated a minimum detectable of R15000 for theft. Since the total replacement cost for cable was R4,945.00. Harmattan note that the incident cost is too low vs the excess required by the insurer. |
| 22/02/2022 | Vergelegen | Block 1, inverter 2, large DC of output current | Inverter 2 had a string fault that caused a high output DC current. It was determined on site that inverter 2, string 2.2.1, had an open circuit voltage reading. The MC4 connection on the module array of string 2.2.1 failed due to a hot connection and melted, causing an open circuit connection. | On 23 February 2022, the MC4 was removed, the cables were reconnected, and a new MC4 was installed and properly connected to ensure continuity. The string was retested and found to be functional. The estimated production loss is 68.85 kWp. |
| 25/05/2022 | Hermanus | Main circuit breakers not switching on | The main circuit breakers at the feeder and PVDB do not want to turn on automatically. It was determined on site that the UFD, which automatically turns the circuit breakers on and off, has failed. | 0n 26 May 2022, the UFD was replaced by another UFD. The production downtime is 900kWp |

Table 9-1: Unscheduled Maintenance Events

## Spare Parts

The following table describes the required maximum spare parts required under the contract vs the minimum spare parts currently available on site.

| Major Parts List – 2022 | Maximum QTY | Durbanville QTY | Vergelegen QTY | Midstream QTY | Hermanus QTY | Highveld QTY |
| --- | --- | --- | --- | --- | --- | --- |
| SUN2000 100KTL Inverter |  | 1 | TBC |  |  | TBC |  | TBC | TBC |  | TBC |  |
| SUN2000 50KTL Inverter |  | 1 | TBC |  |  | TBC |  | TBC | TBC |  | TBC |  |
| 630A CB |  | 1 | TBC |  |  | TBC |  | TBC | TBC |  | TBC |  |
| 200A CB |  | 1 | TBC |  |  | TBC |  | TBC | TBC |  | TBC |  |
| 100A CB |  | 1 | TBC |  |  | TBC |  | TBC | TBC |  | TBC |  |
| Motorised Breaker Mechanism |  | 1 | TBC |  |  | TBC |  | TBC | TBC |  | TBC |  |
| JA Solar 540 W modules |  | 10 | TBC |  |  | TBC |  | TBC | TBC |  | TBC |  |

Table 9-2: Major Spare parts.

The Operator has not provided a spare parts list for each facility. Harmattan has requested these and is now waiting for the Operator's response.

# Project Budget

The purpose of the following table was to show the plant's monthly expenses compared to the allocated budget. However, Harmattan has not yet received a financial model/operating model from the Operator to complete the following table. Harmattan has requested this information from the Operator, and we are still awaiting a response.

| Project Budget |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Site |  | Monitoring | Satellite Data | Site Maintenance & Cleaning | Administration | Spare Parts | Total Cost |
| Durbanville | Forecast | R7'785.83 | R9'673.89 | R37'191.36 | R15'000.00 |  | R69'651.08 |
|  | Actual | TBC | TBC | TBC | TBC | TBC | TBC |
|  | Delta (%) | TBC | TBC | TBC | TBC | TBC | TBC |
| Vergelegen | Forecast | R7'702.96 | R9'673.89 | R36'879.36 | R15'000.00 |  | R69'256.21 |
|  | Actual | TBC | TBC | TBC | TBC | TBC | TBC |
|  | Delta (%) | TBC | TBC | TBC | TBC | TBC | TBC |
| Midstream | Forecast | R2'518.30 | R9'673.89 | R17'360.64 | R15'000.00 |  | R44'552.83 |
|  | Actual | TBC | TBC | TBC | TBC | TBC | TBC |
|  | Delta (%) | TBC | TBC | TBC | TBC | TBC | TBC |
| Tzaneen | Forecast | R4'492.93 | R9'673.89 | R24'794.56 | R15'000.00 |  | R53'961.38 |
|  | Actual | TBC | TBC | TBC | TBC | TBC | TBC |
|  | Delta (%) | TBC | TBC | TBC | TBC | TBC | TBC |
| Highveld | Forecast | R2'906.15 | R9'673.89 | R18'820.80 | R15'000.00 |  | R46'400.84 |
|  | Actual | TBC | TBC | TBC | TBC | TBC | TBC |
|  | Delta (%) | TBC | TBC | TBC | TBC | TBC | TBC |
| Hermanus | Forecast | R2'339.29 | R9'673.89 | R16'686.72 | R15'000.00 |  | R43'699.90 |
|  | Actual | TBC | TBC | TBC | TBC | TBC | TBC |
|  | Delta (%) | TBC | TBC | TBC | TBC | TBC | TBC |
| Totals |  | TBC | TBC | TBC | TBC | TBC | TBC |

Table 10-1: Operating Budget

# Documents Reviewed

| Project Name | Documents Reviewed |
| --- | --- |
| Vergelegen | - Vergelegen April 2022 - Vergelegen February 2022 - Vergelegen December 2021 - Vergelegen July 2022 - Vergelegen June 2022 - Vergelegen March 2022 - Vergelegen January 2022 - Vergelegen November 2022 - Vergelegen August 2022 - SOIR1_Site Operational Incident Report-VMC001-22feb22 - O_M Feedback Report_Vergelegen MC BL1_30-03-22 - O_M Feedback Report_Vergelegen MC BL3_01-04-22 - Thermal Report_Vergelegen MC Block 1_30-03-22 - Thermal Report_Vergelegen MC Block 3_01-04-22 - O_M Inspection Checklist_Vergelegen MC B1_01-04-22 - O_M Inspection Checklist_Vergelegen MC B1_30-03-22 |
| Durbanville | - Durbanville April 2022 - Durbanville February 2022 - Durbanville December 2021 - Durbanville July 2022 - Durbanville June 2022 - Durbanville March 2022 - Durbanville January 2022 - Durbanville August 20222 - SOIR1_Site Operational Incident Report - DMC001 - 10-05-2022 - SOIR1_Site Operational Incident Report - DMC002 - 27-05-2022 - SOIR1_Site Operational Incident Report - DMC003 - 4-07-2022 - O_M Inspection Report_Durbanville MC BL1_20-04-22 - O_M Inspection Report_Durbanville MC BL1_20-04-22 - OMFR_O_M Feedback Report - Durbanville MC Block 1 - 20-04-2022 - OMFR_O_M Feedback Report - Durbanville MC Block 3 - 21-04-2022 - Thermal Report_Durbanville MC Block 1_20-04-22 - Thermal Report_Durbanville MC Block 3_21-04-22 |
| Midstream | - Midstream April 2022 - Midstream February 2022 - Midstream December 2021 - Midstream July 2022 - Midstream June 2022 - Midstream March 2022 - Midstream January 2022 - Midstream November 2022 - Midstream August 2022 |
| Hermanus | - Hermanus April 2022 - Hermanus July 2022 - Hermanus June 2022 - Hermanus May 2022 - Highveld August 2022 - SOIR1_Site Operational Incident Report - HMC001 - 26-05-2022 - Thermal Report_Hermanus Mediclinic_24-08-2022 |
| Highveldf | - Highveld April 2022 - Highveld July 2022 - Highveld June 2022 - Highveld May 2022 - Highveld August 2022 |